## Distributed Layout
DISTRIBUTED LOUDSPEAKER CABLE CALCULATOR
SPL Loss at Last Segment | -0.72981 | dB
SPL Variation | +/- 0,36 | dB
Recommended Amplifier | 500 | W
Max Current | 5.7143 | A
Min Wire Current Headroom | 0.96247 | A
Min Current Headroom is in Segment # 7
Enter "f" for feet or "m" for meters | f | feet
Quantity Spkrs | 40
Cable length | 300 | ft | = 91,4 m
Amplifier to Spkr #1 | 40 | ft | = 12,2 m
Tap | 10 | W
Max Voltage | 70 | V
Segment Length / Spkr | 7.2222 | ft
Total W | 400 | W
Z / Spkr | 490 | ohm |  | NOTES:
Total Spkr Z | 12.25 | ohm |  | Cable Segement 1 is from the Amplifier to Spkr # 1.
Total Cable R | 2.6655 | ohm |  | Suceeding Cable Segements run from Spkr # listed to the next Spkr # listed.
Each Cable Segement is 10% of the cable length minus Cable Segment 1.
The last Cable Segment (10) runs from the last Spkr # listed to the end Spkr = Quantity Spkrs entered.
The Spkr # is the loudspeaker nearest to the beginning of the calculated cable segement length.
Cable Segment | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Enter AWG: | 14 |  |  | 16 |  |  | 18
AWG for Segment | 14 | 14 | 14 | 16 | 16 | 16 | 18 | 18 | 18 | 18
Spkr # | 1 | 5 | 9 | 13 | 17 | 21 | 25 | 29 | 33 | 37
Wire Current Headroom - A | 2.5033 | 3.0748 | 3.6462 | 1.1613 | 1.7327 | 2.3041 | 0.96247 | 1.5339 | 2.1053 | 2.6768
Cable Segment Lengths - ft | 40 | 28.8889 | 28.8889 | 28.8889 | 28.8889 | 28.8889 | 28.8889 | 28.8889 | 28.8889 | 28.8889
Running Total - ft | 40 | 68.8889 | 97.7778 | 126.6667 | 155.5556 | 184.4444 | 213.3333 | 242.2222 | 271.1111 | 300
Cable Segment | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Values At Beginning of Cable Segments
Spkr Load - Qty | 40 | 36 | 32 | 28 | 24 | 20 | 16 | 12 | 8 | 4
Cable R / Segment- ohm | 0.202 | 0.14589 | 0.14589 | 0.23204 | 0.23204 | 0.23204 | 0.36891 | 0.36891 | 0.36891 | 0.36891
Load - ohm | 12.25 | 13.6111 | 15.3125 | 17.5 | 20.4167 | 24.5 | 30.625 | 40.8333 | 61.25 | 122.5
Amperes - A | 5.7143 | 5.1429 | 4.5714 | 4 | 3.4286 | 2.8571 | 2.2857 | 1.7143 | 1.1429 | 0.57143
Loss Ratio Vin/Vout | 0.98378 | 0.9894 | 0.99056 | 0.98691 | 0.98876 | 0.99062 | 0.9881 | 0.99105 | 0.99401 | 0.997
Voltage - V | 68.8644 | 68.1342 | 67.4911 | 66.608 | 65.8595 | 65.2416 | 64.465 | 63.8878 | 63.5053 | 63.3147
dB SPL Loss | -0.14206 | -0.23466 | -0.31703 | -0.43144 | -0.5296 | -0.61147 | -0.71548 | -0.7936 | -0.84576 | -0.87187
dB SPL Ref Spkr #1 | 0 | -0.092603 | -0.17497 | -0.28938 | -0.38754 | -0.46941 | -0.57342 | -0.65154 | -0.7037 | -0.72981
Min Current Headroom | 0.96247 | A
Segment with the Min Current Headroom | # 7

## Wire Table
Data for Standard AWG Wire Gauges
AWG gauge | Diameter Inches | Diameter mm | Ohms per 1000 ft | Ohms per km | Circular Mils | Maximum amps @ 500 circ mils per amp | AWG gauge
0000 | 0.46 | 11.684 | 0.049 | 0.16072 | 211600 | 423.2 | 0000
000 | 0.4096 | 10.4038 | 0.0618 | 0.2027 | 167772.16 | 335.5443 | 000
00 | 0.3648 | 9.2659 | 0.0779 | 0.25551 | 133079.04 | 266.1581 | 00
0 | 0.3249 | 8.2525 | 0.0983 | 0.32242 | 105560.01 | 211.12 | 0
1 | 0.2893 | 7.3482 | 0.1239 | 0.40639 | 83694.49 | 167.389 | 1
2 | 0.2576 | 6.543 | 0.1563 | 0.51266 | 66357.76 | 132.7155 | 2
3 | 0.2294 | 5.8268 | 0.197 | 0.64616 | 52624.36 | 105.2487 | 3
4 | 0.2043 | 5.1892 | 0.2485 | 0.81508 | 41738.49 | 83.477 | 4
5 | 0.1819 | 4.6203 | 0.3133 | 1.0276 | 33087.61 | 66.1752 | 5
6 | 0.162 | 4.1148 | 0.3951 | 1.2959 | 26244 | 52.488 | 6
7 | 0.1443 | 3.6652 | 0.4982 | 1.6341 | 20822.49 | 41.645 | 7
8 | 0.1285 | 3.2639 | 0.6282 | 2.0605 | 16512.25 | 33.0245 | 8
9 | 0.1144 | 2.9058 | 0.7921 | 2.5981 | 13087.36 | 26.1747 | 9
10 | 0.1019 | 2.5883 | 0.9989 | 3.2764 | 10383.61 | 20.7672 | 10
11 | 0.0907 | 2.3038 | 1.26 | 4.1328 | 8226.49 | 16.453 | 11
12 | 0.0808 | 2.0523 | 1.588 | 5.2086 | 6528.64 | 13.0573 | 12
13 | 0.072 | 1.8288 | 2.003 | 6.5698 | 5184 | 10.368 | 13
14 | 0.0641 | 1.6281 | 2.525 | 8.282 | 4108.81 | 8.2176 | 14
15 | 0.0571 | 1.4503 | 3.184 | 10.4435 | 3260.41 | 6.5208 | 15
16 | 0.0508 | 1.2903 | 4.016 | 13.1725 | 2580.64 | 5.1613 | 16
17 | 0.0453 | 1.1506 | 5.064 | 16.6099 | 2052.09 | 4.1042 | 17
18 | 0.0403 | 1.0236 | 6.385 | 20.9428 | 1624.09 | 3.2482 | 18
19 | 0.03589 | 0.9116 | 8.0514 | 26.4154 | 1288.1 | 2.5762 | 19
20 | 0.031961 | 0.8118 | 10.153 | 33.3104 | 1021.5 | 2.043 | 20
21 | 0.028461 | 0.7229 | 12.802 | 42.0013 | 810.1 | 1.62 | 21
22 | 0.025346 | 0.6438 | 16.143 | 52.9626 | 642.44 | 1.2849 | 22
23 | 0.022571 | 0.5733 | 20.356 | 66.7848 | 509.48 | 1.0189 | 23
24 | 0.020102 | 0.5106 | 25.669 | 84.2159 | 404.03 | 0.80821 | 24
Standard AWG and Metric Wire Size Data
Circ. Mils | Equivalent | Awg. | Metric | Stranding/ Wire |  | Approximate
| Circ. Mils | Size | Wire | Dia. per Strand |  | Overall Diameter
Size
|  |  | mm2 | in | mm | in | mm
- | 987 | - | 0.5 | 1 / 0.032 | 1 / 0.813 | 0.032 | 0.81
1020 | - | 20 | - | 7 / 0.0121 | 7 / 0.307 | 0.036 | 0.91
- | 1480 | - | 0.75 | 1 / 0.039 | 1 / 0.991 | 0.039 | 0.99
1620 | - | 18 | - | 1 / 0.0403 | 1 / 1.02 | 0.04 | 1.02
1620 | - | 18 | - | 7 / 0.0152 | 7 / 0.386 | 0.046 | 1.16
- | 1974 | - | 1 | 1 / 0.045 | 1 / 1.14 | 0.045 | 1.14
- | 1974 | - | 1 | 7 / 0.017 | 7 / 0.432 | 0.051 | 1.3
2580 | - | 16 | - | 1 / 0.0508 | 1 / 1.29 | 0.051 | 1.29
2580 | - | 16 | - | 7 / 0.0192 | 7 / 0.488 | 0.058 | 1.46
- | 2960 | - | 1.5 | 1 / 0.055 | 1 / 1.40 | 0.055 | 1.4
- | 2960 | - | 1.5 | 7 / 0.021 | 7 / 5.33 | 0.063 | 1.6
4110 | - | 14 | - | 1 / 0.0641 | 1 / 1.63 | 0.064 | 1.63
4110 | - | 14 | - | 7 / 0.0242 | 7 / 0.615 | 0.073 | 1.84
- | 4934 | - | 2.5 | 1 / 0.071 | 1 / 1.80 | 0.071 | 1.8
- | 4934 | - | 2.5 | 7 / 0.027 | 7 / 0.686 | 0.081 | 2.06
6530 | - | 12 | - | 1 / 0.0808 | 1 / 2.05 | 0.081 | 2.05
6530 | - | 12 | - | 7 / 0.0305 | 7 / 0.775 | 0.092 | 2.32
- | 7894 | - | 4 | 1 / 0.089 | 1 / 2.26 | 0.089 | 2.26
- | 7894 | - | 4 | 7 / 0.034 | 7 / 0.864 | 0.102 | 2.59
10380 | - | 10 | - | 1 / 0.1019 | 1 / 2.59 | 0.102 | 2.59
10380 | - | 10 | - | 7 / 0.0385 | 7 / 0.978 | 0.116 | 2.93
- | 11840 | - | 6 | 1 / 0.109 | 1 / 2.77 | 0.109 | 2.77
- | 11840 | - | 6 | 7 / 0.042 | 7 / 1.07 | 0.126 | 3.21
13090 | - | 9 | - | 1 / 0.1144 | 1 / 2.91 | 0.1144 | 2.91
13090 | - | 9 | - | 7 / 0.0432 | 7 / 1.10 | 0.13 | 3.3
16510 | - | 8 | - | 1 / 0.1285 | 1 / 3.26 | 0.128 | 3.26
16510 | - | 8 | - | 7 / 0.0486 | 7 / 1.23 | 0.146 | 3.7
- | 19740 | - | 10 | 1 / 0.141 | 1 / 3.58 | 0.141 | 3.58
- | 19740 | - | 10 | 7 / 0.054 | 7 / 1.37 | 0.162 | 4.12
20820 | - | 7 | - | 1 / 0.1443 | 1 / 3.67 | 0.144 | 3.67
20820 | - | 7 | - | 7 / 0.0545 | 7 / 1.38 | 0.164 | 4.15
26240 | - | 6 | - | 1 / 0.162 | 1 / 4.11 | 0.162 | 4.11
26240 | - | 6 | - | 7 / 0.0612 | 7 / 1.55 | 0.184 | 4.66
- | 31580 | - | 16 | 7 / 0.068 | 7 / 1.73 | 0.204 | 5.18
33090 | - | 5 | - | 7 / 0.0688 | 7 / 1.75 | 0.206 | 5.24
41740 | - | 4 | - | 7 / 0.0772 | 7 / 1.96 | 0.232 | 5.88
- | 49340 | - | 25 | 7 / 0.085 | 7 / 2.16 | 0.255 | 6.48
- | 49340 | - | 25 | 19 / 0.052 | 19 / 1.32 | 0.26 | 6.6
52620 | - | 3 | - | 7 / 0.0867 | 7 / 2.20 | 0.26 | 6.61
66360 | - | 2 | - | 7 / 0.0974 | 7 / 2.47 | 0.292 | 7.42
- | 69070 | - | 35 | 7 / 0.100 | 7 / 2.54 | 0.3 | 7.62
- | 69070 | - | 35 | 19 / 0.061 | 19 / 1.55 | 0.305 | 7.75